Water supply pipe - maximum operating temperature

Polyethylene (PE) is a thermoplastic material and the strength of the material changes with excessive temperature changes. The specification BS EN12201 Plastic piping systems for water supply and for sewer and drainage under pressure- PE, determines a design operating temperature of 20°C.

In the UK, the normal ground temperature is not expected to exceed 13°C all year round, and with the material design temperature being 20°C, no consideration of the effect of temperature on hoop strength (i.e. operating pressure) is required. The pipe will remain flexible, and the maximum operating pressure is unaffected.

Where the pipe is installed in warmer environments above 20°C such as ducts, tunnels or where the fluid contents increase the operating temperature, a consideration of the thermal effects is required. Where the operating temperature of the pipe is above 20°C for sustained periods, then the maximum pressure rating of the pipeline must be reduced if 50-year design life expectancy is to be maintained. Typically, it is determined that the maximum operating temperature for a PE pipe system is 40°C.

The table below details the corrected maximum operating pressure ratings for common SDR pipes operated at elevated temperatures above 20°C. The derating factor used to calculate the recommended pressure ratings quoted below, is a reduction in pressure of 1.3% per degree Celsius for each degree above 20°C, in accordance with BS EN12201-1 Table A1.

|  | Maximum operating pressure at temperature (bar) |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Material | 20°C | 25°C | 30°C | 35°C | 40°C |
| PE80 SDR11 | 12.5 | 11.7 | 10.9 | - | - |
| PE100 SDR11 | 16.0 | 14.9 | 13.9 | 12.8 | 11.8 |
| PE100 SDR17 | 10.0 | 9.3 | 8.7 | 8.0 | 7.4 |
| PE100 SDR21 | 8.0 | 7.5 | 6.9 | 6.4 | 5.9 |

For Temperature data within the temperatures quoted, interpolation is permitted.

Pressure Testing

When pressure testing Polyethylene pipelines, the lead guidance document is WIS 4-01-03 Specification for hydrostatic pressure testing of Polyethylene water supply pipes. This specification advises that the section of pipeline to be tested should be backfilled and compacted to minimise temperature variance.

Where the pipeline to be tested is exposed to temperatures above 20°C, the system test pressure (STP) applied must consider the maximum operating pressure at the elevated ambient temperature, in accordance with the table above. It should also be considered that pipes exposed to direct sunlight will experience additional solar gain, so actions should be taken to mitigate this.

Document end.